Fire/Smoke Damper

Acceptance Form

(Form FSD-1)

Date:

Time:

INSTALLING CONTRACTOR					PARK INFORMATION

Business Name:							Park Name:

Address:	 							Park Contact:

Representative: 							Contact Phone No:

License No.: 							Building Name/Number:

Telephone:							FMSS Asset ID No.:

*All “No” answers must be explained in Section 5 of this form.

1. DAMPER (FIRE)

General

a. Number installed:

b. Method of Actuation:     Detector        Fusible Link        Link Temperature Rating:

c. Manufacturer:						  Model:

d. All fire dampers installed at locations indicated on 100% construction drawings?     Yes        No

e. All fire dampers labeled “Fire Damper” and painted red?     Yes        No

f. All fire dampers have access doors that facilitate replacement of elements?     Yes        No

g. All fire damper operators are accessible and can be maintained?     Yes        No

h. All damper sleeves secured properly?     Yes        No

Operation

i. Dampers close fully when commanded?     Yes        No

j. Dampers open fully when commanded open?     Yes        No

k. Dampers fail to the proper state upon loss of power?     Yes        No        N/A

l. Damper(s) begin to close within 15 seconds of the time the command is sent from the FACP (where applicable)? Yes   No   N/A

m. Damper(s) are fully closed within 75 seconds of the time the command is sent from FACP (where applicable)?  Yes   No     N/A

n. Damper(s) actuate freely?     Yes        No

o. For 5% of the dampers verify (where applicable):

Wiring is to the correct limit switch   Yes      No      N/A        The limit switch trips when heated   Yes      No      N/A

Limit switch trip temperature (is available):

p. Damper(s) re-open with intervention (where applicable)?     Yes        No        N/A

2. DAMPER (SMOKE)

General (N/A    - If non-applicable proceed to Section 3)

a. Number installed:

b. Method of Actuation:     Detector        Fusible Link        Link Temperature Rating:

c. Manufacturer:						   Model:

d. All smoke dampers installed at locations indicated on 100% construction drawings?     Yes        No

e. All smoke dampers labeled “Smoke Damper” and painted red?     Yes        No

f. All smoke dampers have access doors that facilitate replacement of elements?     Yes        No

g. All smoke damper operators are accessible and can be maintained?     Yes        No

h. All damper sleeves secured properly?     Yes        No

Operation

i. Dampers close fully when commanded?     Yes      No        N/A

j.  Dampers open fully when commanded open?     Yes      No        N/A

k. Dampers fail to the proper state upon loss of power?    Yes      No        N/A

l. Damper(s) begin to close within 15 seconds of the time the command is sent from the FACP?      Yes   No   N/A

m. Damper(s) are fully closed within 75 seconds of the time the command is sent from FACP?       Yes      No        N/A

n. Damper(s) actuate freely?     Yes        No

o. Damper(s) close completely?     Yes        No

p. For 5% of the dampers verify (where applicable):

Wiring is to the correct limit switch     Yes        No             The limit switch trips when heated     Yes        No

Limit switch trip temperature (is available):

q. Damper(s) re-open with intervention (where applicable)?     Yes        No

3. DUCTWORK

a. Ductwork of distribution system completed?     Yes        No

b. Ductwork is free of construction debris and dust inside and outside?     Yes        No

c. Ductwork sizes comply with 100% construction drawing (inside) dimensions?     Yes        No

d. Fire stop sealant materials used where ducts have penetrated fire or smoke rated assemblies?     Yes        No        N/A

e. Ductwork is support by proper hangers?     Yes        No

f. Penetrations of return air ducts in the vicinity of detectors sealed to prevent entrance of outside air?     Yes        No        N/A

4. DETECTORS  (N/A    - If non-applicable proceed to Section 5)

a. Type: 	Area Smoke Detector	     Duct Smoke Detector (interior mount)                 Duct Smoke Detector (exterior mount)

b. Duct detectors are mounted 6 – 10 duct equivalent diameters from an elbow or bend?     Yes        No

c. Detectors mounted in return air ducts are mounted 6 – 10 duct equivalent diameters from return air inlets?    Yes      No      N/A

d. Detectors mounted in supply side air ducts are located upstream of all fans and filters?     Yes        No        N/A

e. Location of all duct detectors is clearly and permanently identified?     Yes        No

f. Duct detectors that employ sampling tubes and are mounted outside of ducts allow for verification of airflow from the duct to the

detector?     Yes        No        N/A

g. Concealed detectors installed more than 10 ft above the floor provided with remote alarm or supervisory indication in a location

acceptable to the AHJ?     Yes        No        N/A

h. Detectors installed where the detector’s alarm or supervisory indicator is not visible are provided with remote alarm or supervisory

indication in a location acceptable to the AHJ?     Yes        No        N/A        Location:

i. All detector inlet tube holes face upstream of airflow?     Yes        No        N/A

j. All return tube slant cuts face downstream of airflow?     Yes        No        N/A

k. Detectors sound an alarm or supervisory signal:     Locally        At the FACP        Both

l. Detector(s) activate damper(s) and shut down air-handling unit(s)?     Yes        No

m. If detector(s) is connected to a sprinkler monitoring panel is detector monitored for power loss?     Yes        No        N/A

n. If detector(s) is connected to a sprinkler monitoring panel can the detector be reset from the FACP

or a LED/reset switch mounted on the ceiling directly below the detector?     Yes        No        N/A

5. COMMENTS:

Signatures

Regional Structural Fire Management Officer (or his designee):

Date:

Contractor:

Date: