GUIDE FOR WRITING OUTLINE SPECIFICATIONS

Based on definitions from the AIA Handbook and the CSI Manual of Practice, an outline specification is an itemized list, using brief, concise statements, of significant materials, systems, and equipment and their criteria and levels of quality. In Addition, any criteria having a special cost impact would be indicated.

Categorize the outline by the appropriate CSI Division, listing all Divisions, even those that are not being used, noting those that will not be used. Also, include Section numbers and titles following the list of possible section numbers and titles found in the CSI Masterformat Master List.

Attached is an example of an outline specification made up of sections from previous projects.  Please note that the materials, methods, and systems included here may not be appropriate for every project. Note also, that some section names and numbers may be out of date. The intention of this example is to provide only a general style and content guide for the preparation of an outline specification. Tailor each outline specification to the specific project.

(Project Name)

(Park Name and Project Number [PMIS No. XXXXXX])

OUTLINE SPECIFICATION

DIVISION 02: EXISTING CONDITIONS

Section not used.

DIVISION 03: CONCRETE

033100  CONCRETE

Use 4,000 psi concrete with a maximum slump of 4". Contractor is responsible for providing the mix design. Use Grade 60 reinforcing steel (epoxy coated when required). Contractor is responsible for all concrete testing (strength, slump, and air content). Actual type and size of footing and foundation system used will be based on soil borings.  Slab on grade floors.

DIVISION 04:  MASONRY

042113  BRICK MASONRY

Brick masonry over metal stud framing and solid masonry where shown.  Mortar ASTM C270.

042200  CONCRETE UNIT MASONRY

ASTM C90, normal weight, Type I, concrete masonry units. Mortar ASTM C270.  Grout ASTM C476, 2000 psi. Reinforcing ASTM A615, Grade 60.

DIVISION 05:  METALS

051200  STRUCTURAL STEEL - GENERAL

Structural steel frame (beams and columns) and miscellaneous members to conform to ASTM A992, 50 ksi. Bolts to conform to either ASTM A307 or A325.  Painting to consist of 1-coat of rust-inhibitive primer.

DIVISION 06:  WOOD, PLASTICS, & COMPOSITES

061000  ROUGH CARPENTRY

Wood furring, sheathing, and blocking for built in casework and nailers for the top of all roof-framing members; minimum 5/8-inch thick structural grade plywood for roof sheathing.

062000  FINISH CARPENTRY

Wood veneer finish casework, solid wood and/or plastic laminate counters, in AWI premium quality for the Information Desk, Sales Area, Library, and Staff Office. Solid wood standing and running trim.

DIVISION 07:  THERMAL AND MOISTURE PROTECTION

072100  BUILDING INSULATION

2-1/2-inch thick (R-11+) extruded polystyrene board perimeter insulation at foundations. R-19 batt insulation for exterior walls. R-38 batt insulation in roofs.

072600  VAPOR RETARDERS

4 mil thick polyethylene under slab on grade and on walls where indicated.

073100  SHINGLES

Mineral fiber cement roof shingles.

074100  METAL ROOFING

2-inch high standing seam, Kynar 500 finished Galvalume metal roofing.

076000  FLASHING AND SHEET METAL

Galvanized sheet metal, painted where exposed.

077200  ROOF ACCESSORIES

Provide continuous metal gravity ridge and fascia ventilators.

079200  JOINT SEALANTS

Use silicone or polyurethane sealants in color to match adjacent surfaces.

DIVISION 8: OPENINGS

081100  METAL DOORS AND FRAMES

Hollow metal doors and frames at toilets, mechanical rooms, and emergency exits.

081400  WOOD DOORS

Provide paneled oak and glass entrance doors with oak frames. On interior, use oak wood veneer solid core wood doors with oak wood frames.

085213  METAL CLAD WOOD WINDOWS

Aluminum clad wood custom windows.

086200  UNIT SKYLIGHTS

Aluminum frame and laminated glass skylight.

087000  HARDWARE

Latch sets, hinges, stops, plates, pulls etc. in oil rubbed and oxidized satin bronze (BHMA 613 or US10B) finish. Use levers on all latch and lock sets, except at service or utility areas use spherical knobs. Master key all locks to the system in use at the park.

088000  GLAZING

Provide 1-inch sealed insulated glass, made up of 1/4-inch thick clear float glass with e2 coating on interior panes of South and East walls. Provide heat mirror glass units on North walls. Use tempered glass where required.

DIVISION 9: FINISHES

092216  NON-STRUCTURAL METAL FRAMING

Metal stud wall and ceiling framing.

092900  GYPSUM BOARD

Use 5/8" regular gypsum board on designated interior walls and on all ceilings.  5/8" water resistant gypsum board in wet areas. Use cementitious glass mesh mortar units on walls designated to have ceramic tile applied. Use Type X gypsum board on partitions requiring fire rating.

093013  CERAMIC TILE

Ceramic mosaic tile walls and quarry tile floors in Toilets (Public and Staff).

096500 RESILIENT FLOORING

Provide resilient flooring in utility, storage, and mechanical spaces.

096813  TILE CARPETING

Continuous filament, soil repellent, recycled material carpet tile with a pile weight of not less than 36 oz. per square yard in Offices, Exhibits, Multipurpose Room, and Library.

099100  PAINTING

Epoxy coatings in toilet rooms, alkyd enamel semi-gloss paints on scheduled walls and ceilings. Use clear stain on interior and exterior wood trim. Ceilings painted white. Meet state volatile organic compound requirements.

DIVISION 10: SPECIALITIES

101400  SIGNAGE

Signs for selected rooms.

102113  TOILET COMPARTMENTS

Floor mounted and overhead braced high-density solid polyethylene partitions with self-closing doors with latches and coat hooks.

102813  TOILET ACCESSORIES

Stainless steel (satin finish) recessed accessories including soap dispensers, towel dispensers, waste receptacles, toilet paper holders, grab bars, feminine napkin dispensers and disposals, and framed glass mirrors.

104400  FIRE PROTECTION SPECIALTIES

Manual extinguishing equipment located in accordance with NFPA 10.

107500  FLAGPOLE

Aluminum flagpole located near front entrance walk.

DIVISION 11: EQUIPMENT

1126000  UNIT KITCHENS

Unit kitchen in Staff Office.

DIVISION 12: FURNISHINGS

122100  WINDOW BLINDS

Vertical blinds in Library and Multipurpose Room.

125651  LIBRARY FURNITURE

Free standing shelving units, study carrels, armchairs, and task lights.

125916  SYSTEMS FURNITURE

Freestanding component systems furniture in offices.

126200  PORTABLE AUDIENCE SEATING

Stackable/ganging chairs and folding tables in Multipurpose Room, color and fabric as selected.

129333 TRASH AND LITTER RECEPTORS

Steel receptacle with top to prevent rain from entering trash bin, including plastic                              trash bin

DIVISION 13: SPECIAL CONSTRUCTION

133400  FABRICATED ENGINEERED STRUCTURES

Provide a pre-engineered single span rigid frame metal building including primary and secondary structural framing, metal roofing and exterior wall covering, doors, windows, insulation, and miscellaneous metal building components and accessories necessary for a complete metal building.

DIVISION 14: CONVEYING EQUIPMENT

Section not used.

DIVISION 21: FIRE SUPPRESSION

211300  FIRE SUPPRESSION SPRINKLER SYSTEMS

Design, furnish, install, and test automatic wet pipe fire sprinkler and standpipe systems for the entire building, including attics, crawl spaces, and concealed spaces in accordance with NFPA 13.

DIVISION 22: PLUMBING

220500  COMMON WORK RESULTS FOR PLUMBING

Materials and methods common to all sections including pipe and equipment identification, seismic restraint systems, pipe hangers and anchors, equipment drives, etc.

220700  PLUMBING INSULATION

Pipe, equipment insulation

221100  FACILITY WATER DISTRIBUTION

### Service weight cast iron waste, vent, and sanitary sewer systems; Type L copper domestic cold and hot water supply systems; and all related equipment accessories and appurtenances.

221123  DOMESTIC WATER PUMPS

Pumping equipment for domestic hot water.

224200  COMMERCIAL PLUMBING FIXTURES

### Low-flow type plumbing fixtures and related trim, fittings, and valves meeting ADA requirements.  Use plumbing fixtures and fittings in accordance with NPS guidelines as follows:

Water Closets -             	1.6 gallons per flush (max)

Urinals -			Waterless

Showerheads -               	2.5 gpm (max) at 80 psi

Kitchen Faucet -            	2.2 gpm (max) at 60 psi

Lavatory Faucet (Public) -  	0.5 gpm (max) at 60 psi

Lavatory Faucet (Private) - 	2.2 gpm (max) at 60 psi

### Wall-hung water closets in the public restrooms. Electronic sensor operated flush valves and faucets in toilets. Freeze-proof drinking fountains located on the exterior of the building with operating mechanisms accessible from the interior of the building. Electric tank-type water heaters located near points-of-use.

DIVISION 23: HEATING, ENTILATING, AND AIR CONDITIONING

230713  DUCT INSULATION

External fiberglass blanket type thermal insulation with fiber-scrim-kraft facing and internal duct acoustical insulation for all supply and outside air ducts, plenums, and return air ducts passing through ambient air or unconditioned spaces.

232113  HYDRONIC PIPING

### Complete and operable hydronic heating system using Type L copper piping.

235200  HEATING BOILERS

### Modular, high efficiency, closed-combustion condensing type gas-fired boilers, flue gas vents, and vent terminations. AL29-4C stainless steel flue gas vents with sidewall vent terminations.

236000  CENTRAL COOLING EQUIPMENT

### Provide packaged air conditioning equipment with indoor condensing units with centrifugal fans, suitable for ducted connections to exterior wall louvers. Provide coatings and fasteners suitable for providing longevity in a coastal environment.  Provide ventilation air during all occupied hours.

233100  HVAC DUCTS AND CASINGS

### Ductwork and appurtenances in connection with HVAC. Spiral-wound round ductwork in exposed ceiling areas; rectangular ductwork in concealed locations such as the mechanical equipment room, chases, or above finished ceilings.

233300  AIR DUCT ACCESSORIES

### Duct accessories such as automatic control dampers, manual control dampers, balancing dampers, fire dampers, turning vanes, flexible duct connections, etc.  Provide heavy-duty two-position dampers immediately behind all air inlet and outlet louvers to close off the louvers openings in a hurricane event.

233713  DIFFUSERS, REGISTERS, AND GRILLS

### Registers, grilles, and diffusers in heating, ventilating, and air conditioning systems.

230593  TESTING, ADJUSTING, AND BALANCING OF HVAC SYSTEMS

### Provide testing apparatus and instruments, and perform all procedures to test, adjust, and balance the various air, fluid, mechanical, and electrical systems associated with the heating, ventilating, and air conditioning systems to optimum performance.

### DIVISION 25: INTERGRATED AUTOMATION

### 255000  INTEGRATED AUTOMATION FACILITY CONTROLS                                                     Building automation and control system for clerestory windows, HVAC, and lighting.

### 255500  INTEGRATED AUTOMATION CONTROL OF HVAC  			            Provide complete electrical/electronic systems of automatic temperature control for the heating, ventilating, and air-conditioning systems in conjunction with the building automation system.

DIVISION 26: ELECTRICAL

260500  COMMON WORK RESULTS FOR ELECTRICAL

### A. Conduit And Fittings:  Rigid steel or intermediate metal conduits. Use compression type conduit fittings, but in trade sizes 3-inch and larger setscrew type connectors will be permitted. Where setscrew type connectors are installed, individual ground wires must be installed along with the circuit conductors.

### B.  Wiring:  All copper 600-volt, type THW insulation except that all wiring running underground or in areas susceptible to moisture shall be rubber insulated type RHW. Wire sizes smaller than #6 AWG solid, sizes #6 and larger stranded. Wiring Devices:  Receptacles 125-volt, 20-ampere specification grade comparable to Hubbell Cat. #5262, or approved equal, single phase, 3-wire, grounding type except as noted otherwise. Snap switches 125-volt, 15-ampere specification grade, silent type.  Metal device plates.

262000  ELECTRICAL DISTRIBUTION

### Run the new 120/208 volt, 3-phase 4-wire 60 hertz service to the high side of the transformer located on the east side of the Visitor Center and Museum. Locate electrical equipment serving site utilities in the electrical equipment room. Locate transformer on concrete pad behind a safety barrier.

262400  SWITCHBOARDS AND PANELBOARDS

Bolt-on type panelboards with ratings exceeding the connected loads and available fault current in accordance with applicable sections of the National Electric Code.  Protect branch circuits serving exterior receptacles or circuits located in toilets, damp, or wet locations with ground fault circuit interrupters.

264100  FACILITY LIGHTNING PROTECTION

Provide lightning protection in accordance with Lightning Protection Institute Standard LPI 175, with concealed copper conductors including protection of trees adjacent to Visitor Center and Museum.

265100  INTERIOR LIGHTING

In compliance with IES, dimmable luminaires on light track in exhibit areas, indirect luminaires in Lobby, cove lighting in Multipurpose Room, task lighting in office areas, flush fluorescent in mechanical rooms and toilets, and both task and flush fluorescent in the Library. Use energy efficient compact fluorescent and T-5 fluorescent lamps where possible.

265600  EXTERIOR LIGHTING

Metal-halide building security and parking lot lighting with high cutoff luminaires to minimize light pollution and glare.

DIVISION 27: COMMUNICATIONS

270500  COMMON WORK RESULTS FOR COMMUNICATIONS

Existing overhead telephone lines will be relocated underground by the telephone company, using the same path and trench as the under-ground power. Provide an empty conduit system for the installation of telephone wiring and equipment by the telephone company. System to consist of all cabinets, pull and junction boxes, bullets, sleeves, fittings, etc. to form a complete telephone system. Extend telephone conduit out to project limit and cap for extension by Telephone Company.

DIVISION 28: ELECTRONICS SAFTEY AND SECURITY

2183100  FIRE DETECTION AND ALARM

Supervised, non-coded, shunt-trip, non-interfering fire conduit, wire, control panels, cabinets, pull stations, automatic fire and smoke detection devices, etc., for an operating fire alarm and smoke detection system.

DIVISION 31: EARTHWORK

311400  CLEARING, GRUBBING, SELECTIVE THINNING AND TREE REMOVAL

Clear and grub stumps and undergrowth. Thin undergrowth and remove trees as directed. Dispose of debris.

312213  SITE AND ROADWAY EXCAVATION AND GRADING

Strip, stockpile and place topsoil. Excavate roadway, embankment, backfill, compact backfill, and place imported borrow. Compact subgrade and do finish grading.

312316  STRUCTURE EXCAVATION

General Site Preparation - Proof roll entire building site after clearing, grubbing, and stripping.  Excavate for foundation and concrete slab-on-grade. After placement of foundation, backfill and compact excavated area utilizing original soil. Density testing will be the responsibility of the Contractor.

312333  TRENCHING AND BACKFILL

Provide trenching and backfilling for utilities

313716  RIPRAP

Furnish and place stone riprap for embankment protection and ends of storm drains.

DIVISION 32: EXTERIOR IMPROVEMENTS

320519  ENGINEERING FABRIC

Furnish and place engineering fabric, landscape fabric, and filter fabric on the subgrade of roads, parking lots, riprap, underdrains, downspouts.

321613  CONCRETE CURBS AND GUTTERS

Concrete and curbs in selected color.

321213  BITUMINOUS PRIME COAT AND TACK COAT

Treat aggregate base course and existing asphalt surfaces with bituminous material.  Include blotting material if required.

321216  ASPHALT PAVING

Construct one or more bituminous surface courses, placed on a prepared base including all pavement transitions and curbs where required.

321236  BITUMINOUS SEAL COAT

Apply bituminous material as a seal coat to a prepared surface.

329213.18  HYDRO SEEDING, FERTILIZING, AND MULCHING

Seed, fertilize, and mulch landscaped areas, roadway shoulders, and steep slopes.

329223  SODDING

Sod lawn areas.

DIVISION 33: UTLITIES

331100  WATER DISTRIBUTION PIPING

Provide a water system including all accessories and piping from the well to the storage tank and then throughout the project. Include fire hydrants, road crossings, and connections to fire protection sprinkler systems.

333113  SEWAGE PIPING

Provide a gravity fed sewage treatment system including accessories, road crossings, and leaching fields.

334213  PIPE CULVERTS

Install new pipe culverts, and end sections.

334413  CONCRETE DROP INLETS AND CATCH BASINS

Construct concrete drop inlets and catch basins with metal grates.

334619  UNDERDRAINS

Install underdrains, pipe, granular filter material, and synthetic fabric.

DIVISION 34: TRANSPORTATION

Section not used.

DIVISION 35: WATERWAY AND MARINE CONSTRUCTION

Section not used.

DIVISION 40: PROCESS INTEGRATION

Section not used.

DIVISION 41: MATERIAL PROCESSING AND HANDLING EQUIPMENT

Section not used.

DIVISION 42: PROCESS HEATING, COOLING, AND DRYING EQUIPMENT

Section not used.

DIVISION 43: PROCESS GAS AND LIQUID HANDLING, PURIFICATION, AND STORAGE EQUIPMENT

Section not used.

DIVISION 44: POLLUTION CONTROL EQUIPMENT

Section not used.

DIVISION 45: INDUSTRY – SPECIFIC MANUFACTURING EQUIPMENT

Section not used.

DIVISION 48: ELECTRICAL POWER GENERATION

Section not used.

End of Outline Specifications